Automated Energy Management System (AEMS) Deployment Preparation Guide

Robert G. Lutes

| Item | Description |
| --- | --- |
| Software | AEMS developed by Pacific Northwest National Laboratory, PNNL |
| Repository | https://github.com/VOLTTRON/volttron-pnnl-aems |
| Document Type | Deployment preparation guide |
| Recommended Operating System | Ubuntu Server 24.04 LTS |
| Supported Edge Hardware | Intel x86_64 or ARM64-based systems |
| Primary Thermostat Integration | BACnet thermostats, typically Wi-Fi-enabled for retrofit applications |
| Example Thermostats | Schneider Electric SE8650 and StratoAutomation OpenStat |
| BACnet Router Reference | https://www.hvacrcontrol.com/language/en/bacnet-router/ |
| Remote Connectivity Option | Tailscale |
| Document Date | 2026-06-22 |
| Document Version | 1.0 |

This document prepares the site, HVAC equipment, thermostats, BACnet network, edge device, and supporting infrastructure for AEMS software deployment.

Table of Contents

1. Purpose and Scope	6

This preparation guide includes the following tasks:	6

2. AEMS Preparation Overview	7

AEMS site preparation	7

3. Pre-Deployment Planning	7

Required pre-deployment information	7

4. Thermostat Deployment	8

4.1 Thermostat Selection Criteria	8

4.2 Schneider Electric SE8650 Example	9

SE8650 standard setup steps	9

4.3 Typical Wi-Fi BACnet Thermostat Example	10

5. Heat Pump Versus RTU Wiring	11

5.1 Conventional RTU Wiring	11

RTU wiring steps:	11

5.2 Heat Pump Wiring	12

Heat pump wiring steps:	12

6. Economizer Considerations	12

6.1 Non-Integrated Economizer Control	13

6.2 Thermostat-Integrated Economizer Control	13

6.3 Economizer Preparation Checks	13

7. Sensor Inputs and Outdoor Air Temperature	14

7.1 OAT Sensor Options	14

7.2 OAT Sensor Installation Guidance	14

7.3 Optional Sensor Inputs	15

8. Network Connectivity Requirements	15

8.1 Edge Device Network Requirements	15

8.2 Thermostat Wi-Fi Requirements	16

8.3 Firewall and Port Requirements	16

9. BACnet Communication and Router Configuration	16

9.1 BACnet/IP Thermostat Addressing	17

9.2 BACnet/IP Thermostat Communication	17

9.3 BACnet MS/TP Thermostat Addressing	18

9.4 BACnet MS/TP Thermostat Communication	18

9.5 Generic BACnet Router Purpose	19

9.6 Generic BACnet Router Configuration Information to Collect	19

BACnet/IP side	20

BACnet MS/TP side	20

Site documentation	20

9.7 Generic BACnet Router Physical Installation	21

9.8 Generic BACnet Router Initial Access	21

9.9 Generic BACnet Router Ethernet and IP Configuration	22

9.10 Generic BACnet Router MS/TP Configuration	23

9.11 BACnet Network Number Planning	24

9.12 BACnet Device Instance Planning	24

9.13 Lumen Wireless BACnet Radio Deployment with BACnet Router	25

9.14 BACnet Router Verification	26

Common BACnet router troubleshooting items	27

9.15 BACnet Router Documentation Template	27

10. Edge Device Requirements	28

Minimum recommended hardware	28

Preferred hardware	29

Installation location guidance	29

11. Installing Ubuntu Server 24.04	29

Update the operating system	30

Install common support utilities	30

12. Configuring Hostname, Time Zone, and NTP	30

Custom NTP configuration	30

13. Installing Docker and Docker Compose as Prerequisites	31

Docker installation commands	31

Optional Docker group configuration	31

14. Security Best Practices	32

Install unattended security updates	32

Recommended SSH settings	32

Firewall setup	32

15. Installing Tailscale for Remote Access	33

Install and start Tailscale	33

Alternative auth-key startup	33

Tailscale best practices	33

16. Reviewing the AEMS Repository	34

Repository review commands:	34

Before proceeding with AEMS software deployment, verify the following	35

17. Pre-Software-Deployment Readiness Checklist	35

17.1 Site Readiness	35

17.2 Thermostat Readiness	35

17.3 BACnet/IP Readiness	36

17.4 BACnet MS/TP Readiness	36

17.5 Edge Device Readiness	37

17.6 Repository Readiness	37

18. Final Preparation Checklist	37

Final handoff note:	38

# 1. Purpose and Scope

The Autonomous Energy Management System (AEMS is software developed by Pacific Northwest National Laboratory (PNNL). AEMS is intended for small- and medium-sized commercial buildings (SMBs), that typically do not have a building automation system (BAS) and use rooftop units (RTUs) for heating, ventilation and cooling. The purpose of AEMS is to provide supervisory features in buildings that would otherwise rely on standalone thermostats.

This document is a deployment preparation guide. It describes preparation of the site, HVAC equipment, thermostats, BACnet communication network, edge device, network connectivity, and supporting infrastructure for AEMS software deployment for retrofit solutions. The actual AEMS software installation, configuration, and runtime instructions come from the official AEMS repository.

AEMS integrates with BACnet-capable thermostats, often using Wi-Fi BACnet/IP thermostats for ease of retrofit. The thermostats continue to provide direct HVAC control for RTUs, and other unitary HVAC equipment. AEMS communicates with the thermostats at a supervisory level for functions such as scheduling, set point management, monitoring, and remote operation.

AEMS does not directly energize or control the compressor, auxiliary heating, fan, or reversing valve. The thermostat remains the local HVAC controller, and AEMS supervises the thermostat through supported BACnet points.

The official AEMS software repository is: https://github.com/VOLTTRON/volttron-pnnl-aems

## This preparation guide includes the following tasks:

The following tasks define the preparation work that should be completed before the AEMS software deployment begins.

- Confirm the HVAC equipment type for each controlled unit.

- Confirm thermostat compatibility and communication method.

- Install and configure BACnet-capable thermostats.

- Confirm RTU or heat pump wiring.

- Confirm economizer control strategy where applicable.

- Provide outdoor air temperature (OAT) input using thermostat-integrated OAT sensors where practical.

- Prepare the site network for thermostat, BACnet, and edge-device communication.

- Configure BACnet/IP, BACnet MS/TP, BACnet router, or Lumen wireless BACnet radio communication as required.

- Install and secure the edge device.

- Install Docker and Docker Compose as prerequisites.

- Clone or review the official AEMS repository when ready.

- Deploy AEMS and apply desired thermostat setting to enable comfort and energy savings features.

# 2. AEMS Preparation Overview

AEMS is intended to bring supervisory control capabilities to SMB buildings without requiring a full BAS retrofit. The preparation process focuses on making the building, thermostats, network, BACnet infrastructure, and edge device ready for the software deployment that will follow.

In most retrofit applications, BACnet thermostats provide the most practical integration point. These thermostats remain responsible for direct HVAC equipment control, while the AEMS deployment communicates through BACnet for supervisory functions.

## AEMS site preparation

A properly prepared site includes the physical equipment, network connectivity, BACnet communication path, and remote access needed to support the later software deployment.

An edge device installed on the site network and prepared with the required operating system and software prerequisites.

BACnet-capable thermostats installed and configured for each RTU, heat pump, or unitary HVAC system.

Wi-Fi BACnet/IP thermostat communication where reliable and permitted by site IT policy.

A BACnet/IP-to-MS/TP router when MS/TP thermostats are used.

Lumen wireless BACnet radios when MS/TP communication is required and physical RS-485 wiring is impractical.

An outdoor air temperature source integrated with one or more thermostats.

Secure remote access, such as Tailscale, if required for support or later deployment activities.

# 3. Pre-Deployment Planning

Before arriving onsite, the deployment team should collect all required site, HVAC, thermostat, BACnet, and network information. Preparation is important because existing thermostat wiring, RTU controls, heat pump behavior, and network restrictions may vary across sites.

## Required pre-deployment information

The following information should be gathered and reviewed before field work begins so that installation and commissioning activities can proceed efficiently.

- Collect the site name, address, customer contact, IT contact, and mechanical contractor contact.

- Identify the edge device installation location.

- Identify each RTU, heat pump, split system, or other controlled HVAC unit.

- Record whether each unit is a conventional RTU or heat pump.

- Record the number of heating and cooling stages for each unit.

- Record whether auxiliary heat or emergency electric heat is present.

- Identify the thermostat model assigned to each HVAC unit.

- Determine whether each thermostat will use Wi-Fi BACnet/IP, wired BACnet/IP, BACnet MS/TP, or MS/TP with Lumen radios.

- Document economizer presence and whether the economizer is thermostat-integrated or controlled by the RTU/economizer controller.

- Identify the outdoor air temperature source and associated thermostat.

- Assign BACnet device instance numbers.

- Assign MS/TP MAC addresses if MS/TP is used.

- Identify the BACnet router location and static IP address if MS/TP is used.

- Review customer IT requirements for Ethernet, Wi-Fi, firewall, DNS, NTP, and remote access.

# 4. Thermostat Deployment

AEMS integrates with BACnet thermostats because they provide a practical retrofit path for SMB buildings. In many buildings, existing thermostats are standalone and do not provide centralized scheduling, remote monitoring, or supervisory control. Replacing those thermostats with BACnet-capable thermostats allows the site to be prepared for BAS-like supervisory features without replacing the HVAC equipment.

The Schneider Electric SE8650 and Strato Automation OpenStat have been used in AEMS-related testing and preparation work so far. The SE8650 is used in this guide as the primary example thermostat because its wiring and settings are known for the intended deployment pattern.

## 4.1 Thermostat Selection Criteria

Thermostat selection should be based on the HVAC equipment type, required communication method, available BACnet objects, and retrofit installation requirements.

The thermostat should support BACnet communication.

The thermostat should support the HVAC equipment type, including conventional RTU or heat pump operation.

The thermostat should expose the BACnet points required by the AEMS deployment.

The thermostat should allow approved supervisory writes, such as set point or occupancy-related commands, when required.

The thermostat should support secure Wi-Fi using WPA2 or WPA3 if Wi-Fi communication is used.

The thermostat should support stable network addressing through static IP assignment or DHCP reservation.

The thermostat should support an OAT input through the thermostat when it is required.

## 4.2 Schneider Electric SE8650 Example

The Schneider Electric SE8650 is the example thermostat for this guide. In this deployment pattern, the SE8650 provides local HVAC control for the RTU or heat pump and exposes BACnet communication for supervisory integration. The thermostat is configured using the known project-standard wiring and settings for the equipment type.

### SE8650 standard setup steps

The following steps describe the project-standard SE8650 setup approach for RTU and heat pump applications.

- Install the SE8650 at the thermostat location serving the corresponding RTU or heat pump.

- https://www.se.com/us/en/download/document/028-0436/

- Land 24 VAC power on R and common on C.

- For a conventional RTU, land cooling stage one on Y1, cooling stage two on Y2 when used, heating stage one on W1, heating stage two on W2 when used, and fan on G.

- For a heat pump, land compressor stage one on Y1, compressor stage two on Y2 when used, fan on G, reversing valve on O/B, and auxiliary or emergency heat on AUX/W or E as applicable.

- Configure the SE8650 Thermostat.

- https://www.se.com/us/en/download/document/028-0442/

- Set the SE8650 equipment type to conventional for RTU applications.

- Set the SE8650 equipment type to heat pump for heat pump applications.

- Set the heat pump reversing valve behavior according to the equipment design.

- Set heating and cooling stage counts according to the connected HVAC unit.

- Set fan operation according to the equipment sequence.

- Connect the SE8650 to the approved OT Wi-Fi or approved organizational Wi-Fi network when Wi-Fi BACnet/IP is used (using VCM8002V5031add-on card installed on thermostat).

- https://download.schneider-electric.com/files?p_enDocType=Instruction+sheet&p_File_Name=028-0497-07_II-VT8000-VCM8002-1.4_EN_RH20220301.pdf&p_Doc_Ref=028-0497

- Do not use guest Wi-Fi, open Wi-Fi, captive portal Wi-Fi, or Wi-Fi networks with client isolation enabled.

- Set or reserve a stable IP address for the thermostat.

- Enable BACnet communication.

- Assign the thermostat a unique BACnet device instance number.

- Use the project-approved BACnet/IP UDP port, typically 47808.

- Map or document the BACnet points required by the AEMS deployment.

- https://www.se.com/us/en/download/document/028-0438/

- Document the thermostat IP address, MAC address, BACnet device instance, HVAC unit served, zone name, and OAT source if applicable.

** Final installation of the SE8650 for AEMS uploading a network heartbeat control script.  The uploader tool instructions, and Lua script are at the following links, respectively:

- https://www.se.com/us/en/download/document/SE8000_Uploader_Tool_Guide/

- https://github.com/VOLTTRON/volttron-pnnl-aems/blob/main/aems-edge/configurations/thermostats/schneider.lua

## 4.3 Typical Wi-Fi BACnet Thermostat Example

A typical Wi-Fi BACnet thermostat used in an AEMS retrofit should function as both the local HVAC controller and the BACnet communication endpoint. This allows the AEMS deployment to supervise HVAC operation without requiring a complete BAS controller installation.

- Install the thermostat at the existing thermostat location when practical.

- Label existing thermostat wires before removing the existing thermostat.

- Verify each conductor by function rather than by wire color.

- Provide 24 VAC power and common to the thermostat.

- Select RTU or heat pump operation in the thermostat configuration.

- Configure heating stages, cooling stages, fan operation, and reversing valve behavior as required.

- Join the thermostat to an approved Wi-Fi network.

- Use secure Wi-Fi only.

- Record the thermostat IP address, MAC address, unit served, zone name, BACnet device instance, and communication type.

- Enable BACnet/IP and document the required BACnet points.

# 5. Heat Pump Versus RTU Wiring

Correct thermostat wiring is essential because the thermostat remains the local HVAC controller. AEMS does not directly energize compressor, heat, fan, or reversing valve. The thermostat must be wired and configured correctly before the site is ready for AEMS software deployment.

## 5.1 Conventional RTU Wiring

A conventional RTU typically uses thermostat outputs for heating, cooling, and fan control. The thermostat is configured as a conventional system rather than a heat pump.

| Terminal | Typical Function |
| --- | --- |
| R | 24 VAC power |
| C | 24 VAC common |
| Y1 | First stage cooling |
| Y2 | Second stage cooling, if present |
| W1 | First stage heating |
| W2 | Second stage heating, if present |
| G | Fan |
| AUX | Optional configurable output |

### RTU wiring steps:

The following steps should be completed when wiring a thermostat for a conventional rooftop unit.

- Review the RTU wiring diagram before removing the existing thermostat.

- Label each existing conductor by terminal function.

- Verify that the transformer has sufficient capacity.

- Connect R and C to provide thermostat power.

- Connect cooling stages to Y1 and Y2 as required.

- Connect heating stages to W1 and W2 as required.

- Connect fan control to G.

- Configure the thermostat for conventional RTU operation.

- Test fan, cooling, and heating operation before the site is handed off for AEMS software deployment.

## 5.2 Heat Pump Wiring

A heat pump uses a reversing valve to switch between heating and cooling operation. This requires heat pump-specific thermostat wiring and configuration.

| Terminal | Typical Function |
| --- | --- |
| R | 24 VAC power |
| C | 24 VAC common |
| Y1 | Compressor stage one |
| Y2 | Compressor stage two, if present |
| G | Fan |
| O/B | Reversing valve |
| AUX/W | Auxiliary heat |
| E | Emergency heat, if present |

### Heat pump wiring steps:

The following steps should be completed when wiring a thermostat for a heat pump application.

- Review the heat pump wiring diagram.

- Determine whether the reversing valve is energized in cooling or heating.

- Label each existing conductor before removal.

- Connect R and C for thermostat power.

- Connect compressor stages to Y1 and Y2 as required.

- Connect fan to G.

- Connect reversing valve to O/B.

- Connect auxiliary or emergency heat if present.

- Configure the thermostat for heat pump mode.

- Configure O/B operation according to the equipment design.

- Test cooling, heating, auxiliary heat, and emergency heat if applicable.

Important: Incorrect O/B configuration can cause a heat pump to heat when cooling is requested or cool when heating is requested. This setting must be tested before the site is considered ready.

# 6. Economizer Considerations

Many RTUs and RTU heat pump systems include economizers. An economizer allows the HVAC unit to use outdoor air for cooling when outdoor conditions are favorable. In many installations, the economizer is controlled by a dedicated RTU controller or economizer controller rather than directly by the thermostat.

The economizer control strategy should be documented during preparation because AEMS may only influence economizer behavior indirectly through thermostat schedules, set points, and cooling calls unless economizer points are exposed through BACnet and used by the implemented AEMS configuration.

## 6.1 Non-Integrated Economizer Control

In a common non-integrated economizer configuration, the thermostat sends a call for cooling. The RTU or economizer controller then determines whether to use outdoor air cooling, mechanical cooling, or a combination of both.

The thermostat typically does not directly modulate the economizer damper.

The RTU or economizer controller handles mechanical cooling staging.

The AEMS deployment influences operation through schedules, set points, occupancy mode, and cooling demand.

Economizer status points should be documented only if they are available and intended for use.

## 6.2 Thermostat-Integrated Economizer Control

Some systems allow the thermostat to participate in economizer control. In this configuration, the thermostat may use outdoor air temperature, mixed air temperature, discharge air temperature, or damper feedback to support the economizer sequence.

- Verify that the thermostat supports economizer control.

- Verify that the RTU or economizer controller allows thermostat-level economizer integration.

- Verify that required sensors are installed and wired.

- Verify that the mechanical contractor has approved the sequence of operation.

- Document all economizer-related BACnet points that may be used by the future AEMS deployment.

## 6.3 Economizer Preparation Checks

Economizer preparation should document how the economizer is controlled and whether any related points will be available for the AEMS deployment.

- Document whether each HVAC unit has an economizer.

- Document whether the economizer is standalone, RTU-controller-based, or thermostat-integrated.

- Verify outdoor air temperature input for the economizer controller if applicable.

- Verify damper operation when site conditions allow.

- Verify that mechanical cooling staging is consistent with the economizer sequence.

- Document any deficiencies for mechanical follow-up before software deployment.

# 7. Sensor Inputs and Outdoor Air Temperature

AEMS benefits from reliable outdoor air temperature information because OAT can support supervisory control decisions, scheduling strategies, and coordination of HVAC operation. Each deployment should include a defined outdoor air temperature source.

The preferred OAT approach is to use a physical outdoor air temperature sensor integrated with a thermostat. The sensor may be installed in one of two common ways.

## 7.1 OAT Sensor Options

Outdoor air temperature may be provided by one thermostat-integrated sensor per unit or by one representative thermostat-integrated sensor for the site.

- Each thermostat may have its own integrated or wired outdoor air temperature sensor. In this arrangement, the OAT sensor associated with each thermostat should be mounted at or near the corresponding RTU or HVAC unit.

- The site may use one representative outdoor air temperature sensor integrated into one thermostat. In this arrangement, the OAT sensor is still connected to a thermostat and mounted at the corresponding RTU or HVAC unit. The future AEMS deployment may use that thermostat’s OAT value as the representative site OAT value if acceptable for the building layout and control strategy.

The deployment team should document which thermostat provides the OAT value used by AEMS. If each thermostat has its own OAT sensor, each sensor and its corresponding HVAC unit should be documented.

## 7.2 OAT Sensor Installation Guidance

Outdoor air temperature sensor placement is important because poor placement can cause the thermostat and future AEMS deployment to use an inaccurate outdoor air value.

- Mount the sensor where it can measure representative outdoor air temperature.

- Mount the sensor at or near the corresponding RTU when it is associated with a specific thermostat.

- Avoid direct sunlight.

- Avoid exhaust air discharge.

- Avoid condenser discharge air.

- Avoid mounting locations affected by roof heat, wall heat, or other local heat sources.

- Use manufacturer-approved sensor wiring and mounting methods.

- Verify that the thermostat reads the OAT sensor correctly.

- Verify that the OAT value is available through the thermostat BACnet points if it will be used later by AEMS.

- Document the thermostat, RTU, sensor location, and BACnet point used for OAT.

## 7.3 Optional Sensor Inputs

Optional sensor inputs may be used when supported by the thermostat and the deployment design. These additional points should only be included in the deployment documentation if they are actually installed, exposed by the thermostat or controller, and intended for use by the AEMS implementation.

Space humidity.

Discharge air temperature.

Mixed air temperature.

Return air temperature.

CO2.

Occupancy.

Equipment status points.

# 8. Network Connectivity Requirements

The edge device requires reliable network connectivity for external management, software prerequisite installation, time synchronization, repository access, and remote support. The preferred configuration is a wired Ethernet connection for the edge device.

Thermostats may communicate over Wi-Fi, BACnet/IP, BACnet MS/TP, or BACnet MS/TP through Lumen wireless BACnet radios. For retrofit applications, Wi-Fi BACnet/IP thermostats are often preferred because they reduce installation labor and avoid pulling new communication wire.

## 8.1 Edge Device Network Requirements

The edge device should have reliable network access before software deployment begins.

- Use wired Ethernet whenever possible.

- Provide outbound internet access.

- Provide reliable DNS.

- Provide reliable NTP time synchronization.

- Allow the edge device to reach thermostat IP addresses or the BACnet router.

- Use a static IP address or DHCP reservation when possible.

- Avoid requiring inbound public firewall ports.

## 8.2 Thermostat Wi-Fi Requirements

Thermostat Wi-Fi should be treated as an operational network connection and should not rely on guest or unsecured wireless networks.

Use WPA2 or WPA3 security.

Use a dedicated OT (operational technology network) SSID when available.

Use organizational Wi-Fi only if it is reliable and properly secured.

Do not use guest Wi-Fi.

Do not use open or unsecured Wi-Fi.

Do not use captive portal Wi-Fi.

Disable client isolation if the edge device must communicate directly with thermostats.

Verify signal strength at each thermostat location.

Use DHCP reservations or static IP addressing when practical.

## 8.3 Firewall and Port Requirements

Firewall and port requirements should be reviewed with site IT before installation so that the edge device, thermostats, and BACnet devices can communicate as required.

TCP 443 outbound for HTTPS, repository access, updates, and remote services.

UDP 123 outbound for NTP.

UDP 41641 outbound for Tailscale direct connectivity when permitted.

UDP 47808 on the local network for BACnet/IP.

DNS access to approved DNS servers.

Note: When Tailscale is used, inbound firewall ports are typically not required. BACnet/IP traffic should generally remain on the local OT or building network.

# 9. BACnet Communication and Router Configuration

AEMS commonly communicates with thermostats using BACnet. In retrofit applications, the preferred approach is often to use Wi-Fi thermostats that support BACnet/IP. This reduces installation labor because no new RS-485 communication wiring is required between thermostats.

Some deployments use BACnet MS/TP thermostats instead of Wi-Fi BACnet/IP thermostats. BACnet MS/TP uses RS-485 communication and requires a BACnet/IP-to-MS/TP router as the edge device communicates over an IP network. A generic BACnet router, such as the router type shown at the following reference link, may be used for this purpose.

BACnet router reference: https://www.hvacrcontrol.com/language/en/bacnet-router/

The BACnet router must connect to the site network using Ethernet. The router should be assigned a static IP address. The preferred static IP address is the gateway subnet with host address .100. For example, if the site gateway is 192.168.1.1, the preferred BACnet router IP address is 192.168.1.100.

Important: The BACnet router is required for BACnet MS/TP thermostat deployments and for BACnet MS/TP deployments that use Lumen wireless BACnet radios. The router bridges BACnet/IP on Ethernet to BACnet MS/TP on RS-485.

## 9.1 BACnet/IP Thermostat Addressing

When thermostats communicate using BACnet over IP, each thermostat IP address shall be configured to match the same subnet as the gateway or router. This addressing convention is intended to make thermostat setup, field verification, AEMS configuration, and future troubleshooting straightforward.

For example, if the gateway or router IP address is 192.168.1.1, then the thermostats should use IP addresses in the same subnet. The last octet should start at 101 for Thermostat 1 and increment by 1 for each additional thermostat.

The BACnet device instance shall correspond to the thermostat number. Therefore, the thermostat with IP address ending in 101 shall have BACnet device instance 1, the thermostat ending in 102 shall have BACnet device instance 2, and so on through the total number of thermostats.

| Thermostat Number | IP Address Example | BACnet Device Instance |
| --- | --- | --- |
| Thermostat 1 | 192.168.1.101 | 1 |
| Thermostat 2 | 192.168.1.102 | 2 |
| Thermostat 3 | 192.168.1.103 | 3 |
| ... | ... | ... |
| Thermostat N | 192.168.1.(100 + N) | N |

For an actual site, use the site gateway or router subnet. For example, if the gateway is 10.20.30.1, then Thermostat 1 should typically be assigned 10.20.30.101 with BACnet device instance 1, Thermostat 2 should be assigned 10.20.30.102 with BACnet device instance 2, and the sequence should continue for all thermostats.

## 9.2 BACnet/IP Thermostat Communication

BACnet/IP thermostats communicate directly over an IP network. This is the simplest communication architecture when the thermostats are Wi-Fi enabled and the site has a reliable OT Wi-Fi or secure organizational Wi-Fi network.

- Verify that the thermostat supports BACnet/IP.

- Connect the thermostat to the approved Wi-Fi or wired IP network.

- Verify that the thermostat receives a valid IP address.

- Verify that the thermostat IP address is in the same subnet as the gateway or router.

- Assign Thermostat 1 an IP address ending in 101, Thermostat 2 an IP address ending in 102, and continue sequentially.

- Assign the BACnet device instance to match the thermostat number.

- Record the thermostat IP address.

- Record the thermostat BACnet device instance number.  Use consistent labelling on the thermostat casing as well as document existing RTU/HP numbering.

- Enable BACnet/IP on the thermostat.

- Use the BACnet/IP UDP port required by the project, typically UDP 47808.

- Verify that the edge device can reach the thermostat network.

- Verify that local firewall rules allow BACnet/IP communication.

- Document the thermostat BACnet points that will be needed for the AEMS deployment.

## 9.3 BACnet MS/TP Thermostat Addressing

When thermostats communicate using BACnet MS/TP, the thermostat remote station address or COM address shall match the BACnet device instance. This convention makes field commissioning easier because the thermostat number, MS/TP address, COM address, and BACnet device instance all match.

Both the MS/TP remote station or COM address and the BACnet device instance shall start at 1 and increment by 1 for each thermostat. For example, Thermostat 1 uses remote station or COM address 1 and BACnet device instance 1. Thermostat 2 uses address 2 and BACnet device instance 2.

| Thermostat Number | MS/TP Remote Station / COM Address | BACnet Device Instance |
| --- | --- | --- |
| Thermostat 1 | 1 | 1 |
| Thermostat 2 | 2 | 2 |
| Thermostat 3 | 3 | 3 |
| ... | ... | ... |
| Thermostat N | N | N |

## 9.4 BACnet MS/TP Thermostat Communication

BACnet MS/TP thermostats communicate over an RS-485 physical network. The edge device cannot normally communicate directly with MS/TP devices unless a BACnet/IP-to-MS/TP router is installed.

- Verify that the thermostats support BACnet MS/TP.

- Install RS-485 communication wiring in a daisy-chain topology.

- Avoid star wiring unless the hardware manufacturer specifically supports it.

- Use shielded twisted pair cable where practical.

- Maintain correct RS-485 polarity throughout the segment.

- Install termination resistors at the two physical ends of the MS/TP segment (not needed for Lumen radio deployments).

- Configure all MS/TP devices for the same baud rate.

- Assign Thermostat 1 remote station or COM address 1, Thermostat 2 address 2, and continue sequentially.

- Assign the BACnet device instance to match the thermostat remote station or COM address.

- Install a BACnet/IP-to-MS/TP router.

- Connect the BACnet router to the site network using Ethernet.

- Assign the BACnet router a static IP address using the preferred .100 address on the gateway subnet when available.

- Configure the BACnet router with the correct IP, BACnet/IP, and MS/TP settings.

- Verify that the router can discover or communicate with the MS/TP thermostats.

Typical MS/TP baud rates include the following common values.

38400

76800

Note: The baud rate must match across the BACnet router, thermostats, and any Lumen wireless BACnet radio (see section 9.13) used on the segment.

## 9.5 Generic BACnet Router Purpose

A generic BACnet router is used to bridge two BACnet networks: the BACnet/IP network used by the edge device and the BACnet MS/TP network used by thermostats or other MS/TP devices. The router does not replace the thermostat and does not control the HVAC equipment.

The router should be installed when thermostats are BACnet MS/TP, when the edge device is on Ethernet or IP, when thermostats are connected by RS-485 wiring, or when thermostats are connected through Lumen wireless BACnet radios that transport MS/TP traffic.

## 9.6 Generic BACnet Router Configuration Information to Collect

Router configuration should be planned before installation so that Ethernet, IP, BACnet/IP, and MS/TP settings are documented and applied consistently.

### BACnet/IP side

The BACnet/IP side defines how the router connects to the Ethernet network used by the edge device.

Router Ethernet connection location.

Router static IP address.

Preferred router static IP address: <gateway subnet>.100.

Example preferred router static IP address: 192.168.1.100 when the gateway is 192.168.1.1.

Subnet mask.

Default gateway.

DNS server if required by the router.

BACnet/IP UDP port, typically 47808.

BACnet/IP network number.

Router BACnet device instance number, if the router exposes one.

Whether the router must be reachable from the edge device subnet.

### BACnet MS/TP side

The BACnet MS/TP side defines how the router communicates with thermostats or other MS/TP devices over RS-485.

MS/TP network number.

MS/TP baud rate.

Router MS/TP MAC address.

Max Master value.

Max Info Frames value, if configurable.

RS-485 polarity.

Termination status.

Biasing requirements, if applicable.

List of thermostat MS/TP remote station or COM addresses.

List of thermostat BACnet device instance numbers.

### Site documentation

The following router information should be recorded so the installation can be supported and reproduced later.

Router manufacturer and model.

Router serial number.

Router firmware version, if available.

Router installation location.

Router power source.

Router Ethernet MAC address.

Router static IP address.

MS/TP segment served.

Thermostats or devices connected to the segment.

Whether Lumen wireless BACnet radios are used.

## 9.7 Generic BACnet Router Physical Installation

Install the BACnet router in a secure and accessible location. The router should be mounted near the MS/TP wiring, Ethernet network connection, and power source when practical.

- Mount the BACnet router in a controls enclosure, mechanical room, or other approved location.

- Provide power according to the router manufacturer’s requirements.

- Connect the Ethernet port of the router to the approved OT network or building controls network.

- Use Ethernet for the router network connection.

- Connect the RS-485 MS/TP terminals to the thermostat MS/TP segment.

- Verify RS-485 polarity. Typical terminals may be labeled + and -, A and B, or D+ and D-.

- Use the same polarity convention across all MS/TP devices.

- Install shielded twisted pair cable where practical.

- Connect cable shield according to the site standard and manufacturer instructions.

- Install end-of-line termination only at the two physical ends of the RS-485 segment.

- Do not install termination at every device.

- Label the router, Ethernet cable, MS/TP cable, and power source.

- Document the router location and connected MS/TP segment.

Note: If the BACnet router is not physically located at the end of the MS/TP segment, its termination setting should normally be disabled unless the manufacturer’s instructions or actual wiring topology require otherwise.

## 9.8 Generic BACnet Router Initial Access

Most generic BACnet routers are configured through a web interface, configuration utility, or local setup connection. The exact access method depends on the router model and firmware.

- Review the router manufacturer’s installation manual.

- Identify the factory default IP address or discovery method.

- Connect a laptop to the same Ethernet network as the router or directly to the router if required.

- Configure the laptop IP address as needed to reach the router’s default IP.

- Open the router web interface or configuration utility.

- Log in using the manufacturer-provided default credentials.

- Change the default password if the router supports local password management.

- Record the final management IP address and credentials according to site security policy.

Important: Do not leave default credentials in place if the router allows password changes.

## 9.9 Generic BACnet Router Ethernet and IP Configuration

The BACnet router should be connected to the site network using Ethernet. The router should be assigned a static IP address so that the edge device can consistently communicate with it. The preferred static IP address is the gateway subnet with host address .100.

For example, if the site gateway is 192.168.1.1 and the subnet is 192.168.1.0/24, assign the BACnet router the static IP address 192.168.1.100 unless that address is already in use or prohibited by the customer’s network plan.

- Connect the BACnet router to the network using Ethernet.

- Set the router to use a static IP address.

- Use <gateway subnet>.100 as the preferred IP address when available.

- Set the subnet mask.

- Set the default gateway.

- Set DNS if required by the router.

- Set the BACnet/IP UDP port, typically 47808.

- Set or verify the BACnet/IP network number.

- Save the configuration.

- Reboot the router if required.

- Verify that the router responds to ping from the commissioning laptop or edge device if ICMP is allowed.

- Verify that the router web interface or management utility is reachable after reboot.

The following example shows typical BACnet router Ethernet and IP documentation values.

Site Gateway: 192.168.1.1

Preferred Router IP Address: 192.168.1.100

Subnet Mask: 255.255.255.0

Default Gateway: 192.168.1.1

BACnet/IP UDP Port: 47808

BACnet/IP Network Number: 1

## 9.10 Generic BACnet Router MS/TP Configuration

The MS/TP side of the router must match the thermostat MS/TP segment.

- Set the MS/TP network number.

- Set the MS/TP baud rate.

- Set the router MS/TP MAC address.

- Set Max Master.

- Set Max Info Frames if configurable.

- Set or verify RS-485 termination settings.

- Verify whether biasing is required or provided by the router.

- Save the configuration.

- Reboot the router if required.

- Verify communication with MS/TP thermostats.

The following example shows typical MS/TP documentation values.

MS/TP Network Number: 2001

MS/TP Baud Rate: 38400

Router MS/TP MAC Address: 0

Max Master: 127

Max Info Frames: 20

Note: The router MS/TP MAC address must be unique on the MS/TP segment. Many deployments use MAC address 0 for the router, but this should be checked against the site addressing plan.

## 9.11 BACnet Network Number Planning

BACnet network numbers must be unique within the routed BACnet system. The BACnet/IP side and BACnet MS/TP side should not use the same network number.

A typical numbering approach is shown below.

BACnet/IP Network Number: 1

MS/TP Network Number: 2001

If there are multiple MS/TP segments, each segment should receive a unique network number.

BACnet/IP Network: 1

MS/TP Segment 1: 2001

MS/TP Segment 2: 2002

MS/TP Segment 3: 2003

## 9.12 BACnet Device Instance Planning

Each BACnet device must have a unique BACnet device instance number. For thermostats, the BACnet device instance should match the thermostat number according to the addressing convention in this section. The BACnet router may use a separate device instance if it exposes a BACnet device object.

The following example shows the preferred thermostat device instance documentation approach.

Router Device Instance, if used: 599001

Thermostat 1 Device Instance: 1

Thermostat 2 Device Instance: 2

Thermostat 3 Device Instance: 3

- Assign a unique BACnet device instance to each thermostat.

- Assign each thermostat BACnet device instance to match the thermostat number.

- Assign a unique device instance to the router if required.

- Avoid duplicate device IDs.

- Record device instance numbers in the site documentation.

- Use the documented device instance numbers during AEMS configuration.

Important: Duplicate BACnet device instance numbers can prevent reliable discovery and communication.

## 9.13 Lumen Wireless BACnet Radio Deployment with BACnet Router

Lumen wireless BACnet radios may be used when pulling RS-485 wire is not practical. In this arrangement, the Lumen radios act as a wireless transport for MS/TP communication. The BACnet router is still required when the edge device communicates over IP and the thermostats are MS/TP devices.

A typical Lumen wireless BACnet radio arrangement is shown below.

AEMS Edge Device

|

| Ethernet / BACnet/IP

|

Generic BACnet Router

|

| RS-485 / BACnet MS/TP

|

Lumen Wireless BACnet Radio Pair

|

| Wireless MS/TP Transport

|

MS/TP Thermostat or MS/TP Segment

- Verify that the thermostat communication type is BACnet MS/TP.

- Install a BACnet/IP-to-MS/TP router on the IP side.

- Connect the BACnet router to the site network using Ethernet.

- Assign the BACnet router a static IP address, preferably <gateway subnet>.100.

- Configure the BACnet router MS/TP baud rate.

- Configure the Lumen radio baud rate to match the MS/TP segment.

- Configure all thermostats on the segment to the same baud rate.

- Assign each thermostat a unique MS/TP remote station or COM address.

- Assign each thermostat BACnet device instance to match the remote station or COM address.

- Pair or configure the Lumen radios according to the manufacturer instructions.

- Verify radio signal strength.

- Avoid installing radios inside sealed metal enclosures unless external antennas or manufacturer-approved methods are used.

- Verify that BACnet discovery or point reads work through the radio link.

- Document the radio locations, radio settings, connected thermostat segment, and BACnet router settings.

## 9.14 BACnet Router Verification

After configuring the router, verify communication before proceeding to AEMS software deployment.

- Verify the router is powered.

- Verify Ethernet link status.

- Verify the router static IP address.

- Verify the static IP follows the preferred <gateway subnet>.100 convention where available.

- Verify the commissioning laptop or edge device can ping the router if ICMP is allowed.

- Verify the router web interface or configuration utility is reachable.

- Verify BACnet/IP UDP port configuration.

- Verify BACnet/IP network number.

- Verify MS/TP network number.

- Verify MS/TP baud rate.

- Verify router MS/TP MAC address.

- Verify thermostat MS/TP remote station or COM addresses.

- Verify thermostat BACnet device instance numbers.

- Verify thermostat BACnet device instances match thermostat numbers.

- Verify RS-485 polarity.

- Verify termination at only the two ends of the MS/TP segment.

- Verify Lumen radio communication if radios are used.

- Verify BACnet device discovery using an approved BACnet tool or the later AEMS commissioning process.

### Common BACnet router troubleshooting items

If MS/TP devices are not discovered or communication is intermittent, the following items should be checked first.

Incorrect MS/TP baud rate.

Reversed RS-485 polarity.

Duplicate MS/TP remote station or COM addresses.

Duplicate BACnet device instance numbers.

MS/TP remote station or COM address does not match the BACnet device instance.

Missing or excessive termination.

Incorrect BACnet network numbers.

Router IP address on the wrong subnet.

Router not connected by Ethernet to the correct network.

Router static IP address conflict.

Firewall blocking BACnet/IP UDP 47808.

Lumen radio signal or pairing issue.

Thermostat BACnet not enabled.

## 9.15 BACnet Router Documentation Template

The following information should be recorded for each BACnet router before software deployment begins.

Site Name:

Router Location:

Router Manufacturer:

Router Model:

Router Serial Number:

Router Firmware Version:

Ethernet MAC Address:

Router Ethernet Connection Location:

Router Static IP Address:

Preferred IP Used (<gateway subnet>.100): Yes / No

Subnet Mask:

Default Gateway:

BACnet/IP UDP Port:

BACnet/IP Network Number:

MS/TP Network Number:

MS/TP Baud Rate:

Router MS/TP MAC Address:

Max Master:

Max Info Frames:

Termination Enabled at Router: Yes / No

Biasing Provided by Router: Yes / No / Unknown

Lumen Radios Used: Yes / No

Lumen Radio Location 1:

Lumen Radio Location 2:

Radio Baud Rate:

Radio Signal Strength Verified: Yes / No

Connected Thermostats:

- Thermostat Name:

Thermostat Number:

HVAC Unit:

BACnet/IP Address, if used:

MS/TP Remote Station / COM Address, if used:

BACnet Device Instance:

OAT Sensor Connected: Yes / No

Notes:

Note: This documentation should be completed before the AEMS software deployment begins.

# 10. Edge Device Requirements

The edge device hosts the local software stack after AEMS is deployed. During preparation, the edge device should be installed, networked, secured, and loaded with required prerequisites.

## Minimum recommended hardware

The following minimum hardware specifications are suitable for basic edge device preparation.

Two CPU cores.

4 GB RAM.

32 GB storage.

One Ethernet port.

Intel x86_64 or ARM64 architecture.

## Preferred hardware

The preferred hardware specifications provide additional capacity and reliability for production deployments.

Four CPU cores.

8 GB RAM or more.

64 GB SSD storage or more.

Wired Ethernet.

Industrial or commercial-grade power supply.

UPS backup where practical.

## Installation location guidance

The edge device should be installed in a secure and serviceable location that supports reliable network and power connections.

- Install the device in a secure mechanical room, IT closet, or controls enclosure.

- Provide stable power.

- Use wired Ethernet when available.

- Avoid excessive heat, moisture, dust, and vibration.

- Ensure adequate ventilation.

- Label the device with the site name, hostname, and support contact if required.

- Document the device serial number, Ethernet MAC address, and IP address.

# 11. Installing Ubuntu Server 24.04

Ubuntu Server 24.04 LTS is the preferred operating system for new AEMS edge device preparations. All the instruction in this document were tested with Ubuntu Server 24.04

- Download Ubuntu Server 24.04 LTS from the official Ubuntu website.

- Create bootable USB installation media.

- Boot the edge device from the USB installer.

- Follow the installation prompts.

- Create the administrative user account.

- Enable OpenSSH during installation.

- Configure network access using DHCP initially unless a static IP is already assigned.

- Complete the installation.

- Reboot the edge device.

## Update the operating system

After Ubuntu is installed, update the operating system before installing additional prerequisites.

sudo apt update

sudo apt upgrade -y

sudo reboot

## Install common support utilities

The following utilities are commonly useful for repository access, troubleshooting, editing files, and validating system configuration.

sudo apt update

sudo apt install -y ca-certificates curl gnupg lsb-release vim nano git unzip jq openssl

# 12. Configuring Hostname, Time Zone, and NTP

The edge device should have a clear hostname that identifies the site and device role. A recommended naming format is aems-[site-id]-edge01.

sudo hostnamectl set-hostname aems-site001-edge01

hostnamectl

Accurate time is required for schedules, logs, certificates, data timestamps, and remote communication. Set the correct time zone and enable NTP synchronization.

timedatectl status

sudo timedatectl set-ntp true

sudo timedatectl set-timezone America/New_York

## Custom NTP configuration

Use a preferred time synchronization service to use; however, this document describes how to configure time synchronization using a publicly NTP servers.

sudo nano /etc/systemd/timesyncd.conf

[Time]

NTP=pool.ntp.org

FallbackNTP=time.cloudflare.com time.google.com

sudo systemctl restart systemd-timesyncd

timedatectl status

# 13. Installing Docker and Docker Compose as Prerequisites

This guide includes Docker installation as an edge-device preparation step only. The actual AEMS container names, Docker Compose files, configuration files, environment variables, volumes, and runtime commands must come from the official PNNL AEMS repository documentation.

Important: Do not create arbitrary AEMS Docker Compose files or configuration files. Use only the files and instructions provided by the official repository.

Docker should be installed from Docker’s official repository rather than from the default Ubuntu Docker package.

## Docker installation commands

Use the following commands to install Docker Engine and the Docker Compose plugin from Docker’s official repository.

sudo apt remove -y docker docker-engine docker.io containerd runc

sudo apt update

sudo apt install -y ca-certificates curl

sudo install -m 0755 -d /etc/apt/keyrings

sudo curl -fsSL https://download.docker.com/linux/ubuntu/gpg -o /etc/apt/keyrings/docker.asc

sudo chmod a+r /etc/apt/keyrings/docker.asc

echo "deb [arch=$(dpkg --print-architecture) signed-by=/etc/apt/keyrings/docker.asc] https://download.docker.com/linux/ubuntu $(. /etc/os-release && echo $VERSION_CODENAME) stable" | sudo tee /etc/apt/sources.list.d/docker.list > /dev/null

sudo apt update

sudo apt install -y docker-ce docker-ce-cli containerd.io docker-buildx-plugin docker-compose-plugin

sudo systemctl enable docker

sudo systemctl start docker

sudo docker version

sudo docker compose version

sudo docker run hello-world

## Optional Docker group configuration

The deployment user may be added to the Docker group if the site allows Docker commands to be run without sudo.

sudo usermod -aG docker $USER

Note: Log out and log back in before running Docker commands without sudo.

# 14. Security Best Practices

The edge device should be secured as production infrastructure. The device may have access to HVAC control networks and should not be treated as a general-purpose workstation.

Keep the operating system patched.

Use SSH keys instead of passwords.

Disable root SSH login.

Disable password SSH login after key access is verified.

Enable a firewall.

Avoid exposing services directly to the public internet.

Use Tailscale or another approved VPN for remote access.

Restrict access to sensitive files.

Avoid storing credentials in source control.

Limit open ports to required services only.

- A more comprehensive cyber security guide was also created to accompany this guide.

## Install unattended security updates

Unattended security updates help keep the edge device patched after it is placed into service.

sudo apt install -y unattended-upgrades

sudo dpkg-reconfigure unattended-upgrades

## Recommended SSH settings

SSH should be configured to reduce the risk of unauthorized remote access.

PermitRootLogin no

PasswordAuthentication no

PubkeyAuthentication yes

Restart the SSH service.

sudo systemctl restart ssh

## Firewall setup

The firewall should be enabled after required management access has been verified.

Install nftables and disable ufw.

sudo apt install -y nftables

sudo systemctl stop ufw

sudo systemctl disable ufw

Configure and restart nftables.

sudo tee /path/to/your/file > /dev/null <<'EOF'

#!/usr/sbin/nft -f

flush ruleset

add table ip filter

add chain ip filter INPUT { type filter hook input priority 0; policy accept; }

add chain ip filter FORWARD { type filter hook forward priority 0; policy accept; }

add chain ip filter OUTPUT { type filter hook output priority 0; policy accept; }

add rule ip filter INPUT iifname "lo" counter accept

add rule ip filter INPUT ct state related,established counter accept

add rule ip filter INPUT icmp type { echo-request } limit rate 5/second accept

add rule ip filter INPUT tcp dport 22 counter accept

add rule ip filter INPUT udp dport 47808 counter accept

add rule ip filter INPUT tcp dport 8443 counter accept

add rule ip filter INPUT tcp dport 443 counter accept

add rule ip filter INPUT udp dport 123 counter accept

add rule ip filter INPUT counter drop

EOF

sudo systemctl restart nftables

# 15. Installing Tailscale for Remote Access

Tailscale can be used for secure remote management and data transport. It is especially useful for AEMS preparation and deployment support because it does not require inbound firewall ports to be opened at the customer site.

## Install and start Tailscale

Use the following commands to install Tailscale and connect the edge device to the approved Tailnet.

curl -fsSL https://tailscale.com/install.sh | sh

sudo tailscale up

tailscale status

tailscale ip -4

## Alternative auth-key startup

An auth key may be used when interactive login is not practical or when devices are pre-authorized by the administrator.

sudo tailscale up --authkey <TAILSCALE_AUTH_KEY> --hostname aems-site001-edge01

## Tailscale best practices

Tailscale should be configured according to the organization’s access control and device management policy.

Use a hostname that identifies the site and edge device.

Use access control lists to restrict access.

Use tags for production devices when appropriate.

Disable key expiry only when allowed by policy.

Avoid granting broad administrative access.

Verify that the device appears in the Tailscale admin console.

# 16. Reviewing the AEMS Repository

The official AEMS software repository is maintained under the VOLTTRON GitHub organization. This preparation guide does not provide the AEMS software deployment procedure. The actual software installation, configuration, Docker Compose files, scripts, container names, environment variables, and runtime commands must come from the official repository documentation.

Official repository: https://github.com/VOLTTRON/volttron-pnnl-aems

## Repository review commands:

The following commands prepare a local copy of the official AEMS repository so the deployment team can review the repository-provided instructions.

sudo mkdir -p /opt/aems

sudo chown -R $USER:$USER /opt/aems

cd /opt/aems

git clone https://github.com/VOLTTRON/volttron-pnnl-aems.git .

If the repository has already been cloned, update it.

cd /opt/aems

git pull

After the repository is cloned or updated, review the files at the repository root.

cd /opt/aems

ls -la

The following command can be used to search for repository documentation files.

find . -maxdepth 3 -type f \( -iname "README*" -o -iname "*.md" \)

The following command can be used to search for deployment-related files provided by the repository.

find . -maxdepth 3 -type f \( \

-iname "docker-compose.yml" -o \

-iname "compose.yml" -o \

-iname "docker-compose*.yml" -o \

-iname "Makefile" -o \

-iname ".env.example" -o \

-iname ".env.template" \

\)

## Before proceeding with AEMS software deployment, verify the following

The following items should be complete before the actual software deployment begins.

- The edge device operating system is installed and updated.

- Docker and Docker Compose are installed if required by the repository.

- Network connectivity is working.

- Time synchronization is working.

- Thermostat communication has been prepared.

- BACnet/IP or BACnet MS/TP communication has been prepared.

- BACnet router configuration is documented if MS/TP is used.

- BACnet router Ethernet connection and static IP address are documented if MS/TP is used.

- OAT sensor source is documented.

- Tailscale or another remote access method is working if required.

- The official repository documentation has been reviewed.

Important: Do not create arbitrary AEMS configuration files unless the repository documentation instructs you to do so.

# 17. Pre-Software-Deployment Readiness Checklist

This checklist should be completed before beginning the actual AEMS software deployment from the official repository.

## 17.1 Site Readiness

The site readiness checklist verifies that building, equipment, and IT information has been collected.

Site information has been collected.

HVAC equipment inventory has been completed.

RTU or heat pump type has been documented for each unit.

Economizer presence and control strategy have been documented.

OAT source has been identified.

OAT sensor location has been documented.

Site IT requirements have been reviewed.

## 17.2 Thermostat Readiness

The thermostat readiness checklist verifies that thermostats are installed, configured, and prepared for BACnet communication.

Thermostat model has been selected for each HVAC unit.

Schneider SE8650 or other approved Wi-Fi BACnet thermostat configuration has been reviewed.

Thermostats are powered.

Thermostat wiring has been verified.

Thermostats are configured for RTU or heat pump operation.

Heating and cooling stages are configured.

Heat pump reversing valve settings are configured if applicable.

Auxiliary heat is configured if applicable.

Thermostat Wi-Fi connectivity is verified if Wi-Fi is used.

BACnet is enabled on each thermostat.

BACnet device instance numbers are unique.

## 17.3 BACnet/IP Readiness

The BACnet/IP readiness checklist applies when thermostats communicate directly over an IP network.

Thermostat IP addresses are documented.

Edge device can reach thermostat network.

BACnet/IP UDP port is documented.

Client isolation is disabled if direct communication is required.

Required thermostat BACnet points are known or documented.

## 17.4 BACnet MS/TP Readiness

The BACnet MS/TP readiness checklist applies when thermostats communicate over RS-485, including deployments that use Lumen wireless BACnet radios.

BACnet router is installed if MS/TP thermostats are used.

BACnet router is connected to the site network via Ethernet.

BACnet router static IP address is documented.

Preferred router IP address of <gateway subnet>.100 was used if available.

BACnet/IP network number is documented.

MS/TP network number is documented.

MS/TP baud rate is documented.

Router MS/TP MAC address is documented.

Thermostat MS/TP MAC addresses are unique.

Thermostat BACnet device instance numbers are unique.

RS-485 polarity has been verified.

MS/TP termination has been verified.

Lumen wireless BACnet radios have been configured and tested if used.

## 17.5 Edge Device Readiness

The edge device readiness checklist verifies that the local compute platform is installed, secured, and prepared with required prerequisites.

Edge device is installed in the approved location.

Edge device has stable power.

Edge device has wired Ethernet where available.

Ubuntu Server 24.04 LTS is installed. It should work on other Ubuntu LTS version, but the features in this guide were tested with version 24.04.

Hostname is configured.

Time zone is configured.

NTP synchronization is active.

Operating system is updated.

Docker is installed from Docker’s official repository if required.

Docker Compose plugin is installed if required.

Firewall is configured.

SSH is secured.

Tailscale is installed and connected if used.

## 17.6 Repository Readiness

The repository readiness checklist verifies that the official AEMS repository has been reviewed before software deployment begins.

Official AEMS repository has been identified.

Repository documentation has been reviewed.

Deployment files have been identified.

Required configuration files have been identified from the repository.

No unsupported or arbitrary configuration files have been created.

Software deployment is ready to proceed using repository instructions.

# 18. Final Preparation Checklist

Before handing off to the AEMS software deployment process, verify that all preparation work is complete.

The edge device is installed and online.

The edge device has internet access.

DNS resolution works.

NTP synchronization works.

Docker is installed if required.

Tailscale or approved remote access works if required.

Thermostats are installed and powered.

Thermostats are configured for the correct HVAC equipment type.

Thermostat Wi-Fi or BACnet communication is prepared.

BACnet device instance numbers are unique.

BACnet MS/TP router is configured if required.

BACnet router is connected to the network via Ethernet if required.

BACnet router has a static IP address, preferably <gateway subnet>.100.

Lumen wireless BACnet radios are configured if required.

Outdoor air temperature source is documented.

Economizer strategy is documented.

Network and firewall requirements are documented.

Repository documentation has been reviewed.

The site is ready for AEMS software deployment using official repository instructions.

## Final handoff note:

The following note may be used to document that preparation is complete and that the next step is repository-based AEMS software deployment.

This site has been prepared for AEMS software deployment.

The next step is to deploy and configure AEMS using the official instructions from:

https://github.com/VOLTTRON/volttron-pnnl-aems